Index

- Specification No. K/R&D/SMCTO-01 Rev (01).                	dated                 20th Mar, 2012

2.	Specification No. K/R&D/SMCTO-01 Rev (02).                	dated		14th Nov, 2012

Specification for PT/CT Operated Static Multi-Tariff AMR Energy Meters

- Foreword

0.1	This specification has been prepared by Research & Development Department.

0.2	This Specification is intended for the purpose of technical specification only for the 	procurement of material and does not include provisions of contract, unless otherwise provided in 	the contract.

  - This Specification is subject to revision as and when required.

1.0	Scope

1.1	This specification is intended for the purpose of technical scrutiny for the procurement of 	HT and 	LT Static AC Energy Meter with AMR , class-0.5S to be used for billable consumers.

1.2	The Specification covers Multi Rate (Time of day) solid state three phase energy meters 	capable of 	measuring MDI-KW, KWH, & KVARH along with other quantities and built-in 	programmable 	features mentioned in this specification.  The meter shall record and display all these quantities in 	programmable TOD periods along with other features mentioned in the specification hereunder:

1.3	HT type PT & CT operated AMR meters with Communication modem capable to be programmed 	both for 3-Phase, 3-Wire, 2-Element OR 3-Phase, 4-Wire, 3-Element system to utilize the same 	meter   according to the system requirement, 5/10 Amp, 50 Hz, Accuracy Class 0.5S-Energy Meters.

1.4	LT type CT operated 3-Phase, 4-Wire, 3-Elements, 3x230/400 V, 5(10) Amp, 50 Hz Accuracy 	Class 0.5S-AMR Energy Meters with Communication modems.

1.5   	Details of AMM system, billing engine & communication module are provided in Annex II.

2.0	Reference Standards

The Reference standards are listed and provided in Annex-1.  Latest version to be referred

### 3.0	Definitions

3.1	Static Watt-Hour Meter

Meter in which current and voltage act on solid state (electronic) elements to produce and output proportional to watt-hour

3.2	Multi-Rate Meter

Energy meter provided with a number of registers, each becoming operative at specified time intervals corresponding to different tariffs.

  - Measuring Element

Part of the meter which produces an output proportional to the energy

3.4	Test Output

Device which can be used for testing the meter

3.5	Operational Indicator

Device which gives a visible signal of the operation of the meter

3.6	Memory

Element which stores digital information

3.7	Non-Volatile Memory

#### Storage device which can retain information in the absence of power

3.8	Display

Device which displays the content of the memories

3.9	Register

Electronic device comprising both memory and display which stores and displays information

3.10	Current Circuit

Internal connections of the meter and part of the measuring element through which flows the current of the circuit to which the meter is connected.

3.11	Voltage Circuit

Internal connections of the meter, part of the measuring element and power supply for the meter supplied with the voltage of the circuit to which the meter is connected.

3.12	Auxiliary Circuit

Elements (lamps, contacts, etc.) and connection of an auxiliary device with-in the meter case intended to be connected to an external device for example clock, relay, impulse counter.

3.13	Constant

Value expressing the relation between the energy registered by the meter and the corresponding value of the test output.  If this value is a number of pulses, the constant should be either pulses per kilowatt-hour (imp/kWh) or watt hours per pulse (Wh/imp).

3.14	Base

Back of the meter by which it is generally fixed and to which are attached the measuring element, the terminals or the terminal block, and the cover.

3.15	Cover

Enclosure on the front of the meter, made either wholly of transparent material or opaque material provided with window (s) through which the operational indicator (if fitted) and the display can be read.

3.16	Case

Comprises the base and the cover

3.17	Protective Earth Terminals

Terminal connected to accessible conductive parts of the meter for safety purposes.

3.18	Terminal Block

Support made of insulating material on which all or some of the terminals of the meter are grouped together.

3.19	Terminal Cover

Cover which covers the meter terminals and generally, the ends of the external wires or cables connected to the terminals.

3.20	Clearance

Shortest distance measured in air between two conductive parts.

3.21	Creepage Distance

Shortest distance measured over the surface of insulation between two conductive parts.

3.22	Basic Insulation

Insulation applied to live parts to provide basic protection against electric shock.

3.23	Rated Current (In)

Value of current in accordance with which the relevant performance of a transformer operated meter is fixed.

3.24	Maximum Current (Imax)

Highest value of current at which the meter purports to meet the accuracy requirements of this standard

3.25	Reference Voltage (Un)

Value of the voltage in accordance with which the relevant performance of the meter is fixed

3.26	Reference Frequency

Value of the frequency in accordance with which the relevant performance of the meter is fixed

3.27	Percentage Error

Percentage error is given by the following formula:

Percentage error = Energy registered by the meter – True energy        x 100

True energy

Since the true value cannot be determined, it is approximated by a value with a stated uncertainly that can be traced to standards agreed upon between manufacturer and user or to national standards.

3.28	Reference Conditions

Appropriate set of influence quantities and performance characteristics, with reference values, their tolerance and reference ranges, with respect to which the intrinsic error is specified.

3.29	Electromagnetic Disturbance

Conducted or radiated electromagnetic interference which may affect functionally or meteorologically the operation of the meter.

3.30	Rated Operating Conditions

Set of specified measuring ranges for performance characteristics and specified operating ranges for influence quantities, within which the variations or operating errors of a meter are specified and determined.

3.31	Specified Measuring Range

Set of values of a measured quantity, which forms a part of the rated operating conditions.

3.32	Specified Operating Range

Range of values of a single influence quantity, which forms a part of the rated operating conditions

3.33	Limit Range of Operation

Extreme conditions which an operating meter can withstand without damage and without degradation of its meteorological characteristics when it is subsequently operated under its rated operating conditions

3.34	Storage & Transport Conditions

Extreme conditions which a non-operating meter can withstand without damage and without degradation of its meteorological characteristics when it is subsequently operated under its rated operating conditions

3.35	Normal Working Position

Position of the meter defined by the manufacturer for normal services

3.36	Thermal Stability

Thermal stability is considered to be reached when the change in error as a consequence of thermal effects during 20 minutes is less than 0.1 times the maximum permissible error for the measurement under consideration.

4.0	Climatic Conditions

a).	Peak ambient temperature			50oC

b).	Mean max. temperature during 24 hours		45oC

c).	Minimum temperature				0oC

d).	Maximum relative humidity			95 oC (dry bulb 43 oC).

e).	Average annual rain fall				150 mm

f).	Altitude					Mean sea level

g).       Location                                                          	Sea coast with semi desert interior and   									marshy soil near the coastal area.

5.0	Construction & Design Details:

5.1	General

HT type PT & CT operated meters capable to be programmed both for 3 phase, 3 wire, 2 element OR 3 phase, 4 wire, 3 element system to utilize the same meter according to the system requirement, 5/10 Amp, 50 Hz, Accuracy Class 0.5S-AMR Energy Meters with Communication  modems.,

The 400/415 Volts Low Voltage meter shall consist of 3-phase, 4-wire, CT operated two-part tariff meter suitable for unbalanced load.

The meters shall provide immunity to the following levels as stated in test procedure under latest IEC where appropriate.

- 	Impulse Voltage test				6 KV

- 	AC Voltage test					4 KV

-	Current overload (0.5 second)			20 Imax

-	Current overload (permanent)			200% Imax

The meters shall be capable of maintaining desired accuracy at the following operating temperature range.

- 	Normal						- 10 C to + 55 C

-	Short duration 					- 20 C to + 60 C

Line voltage variation tolerance shall be within the limits of – 20% to + 15% of nominal value.

5.2	Mechanical Requirements

Meters shall be designed and constructed in such a way as to avoid introducing any danger in normal use and under normal conditions, so as to ensure especially:

-	Personal safety against electric shock

-	Personal safety against effects of excessive temperature.

-	Protection against spread of fire.

-	Protection against penetration of solid objects, such as thin wire. X-ray film.

-	Dust and water proof.

All parts which are subject to corrosion under normal working conditions shall be protected effectively. Any protective coating shall not be liable to damage by ordinary handling nor damage due to exposure to air, under normal working conditions.  Meters shall withstand solar radiation.

5.3	The electrical connections in the meter shall be resistant to tampering.  These shall be made so as to prevent their opening from outside the meter base/cover accidentally or deliberately without breaking the seals.

5.4	Case

5.4.1	The meter shall have a dust proof and moisture proof case which can be sealed in such a way that the internal parts of the meter are accessible only after breaking the seals. The meter shall comply with the dust proof and water proof IP-54 requirements of IEC-529 (latest edition).

5.4.2	Meter Cover

The cover of meter shall be made of strong metallic/insulating materials with transparent window. Arrangement for scroll knob / push button and optical communication interface shall be provided in the cover/reading window having access from outside. The joints at window and resetting device shall not allow ingress of thin wire/film or similar objects.

5.4.3	Meter Base

The base of the meter shall either be made of metal or strong insulating materials.

  - Terminals – Terminal Block

5.5.1	The terminals shall be grouped in a terminal block having adequate insulating properties and 	mechanical strength. The material (Bakelite or similar material) of which the terminal block is 	made shall be capable of passing the glow wire test of 960oC, while terminal cover and meter case 	shall be capable of passing 650oC temperature test as per IEC-62052-11 (latest edition).

5.5.2	Arrangements may be provided to prevent the exit of terminal block by force from outside without opening the meter cover.

5.5.3	The terminal shall be of bore type to accommodate up-to 5mm dia copper conductor.

  - Earthing Connection Arrangement

5.6.1	If the base is of insulating material, the common ground of the main PCB shall be internally 	connected to the neutral point of the terminal block or on a separate terminal.

5.6.2	If the base is of metallic/conducting material, the common ground point of the PCB shall also be electrically connected to the external earth terminal, (which shall be clearly identified by the earthing symbol), as well as to the neutral point of the terminal block.

5.7	Terminal Block Cover

5.7.1	A sealable terminal block cover of insulating material shall be provided.  No access to the 	terminals shall be possible without breaking the seals.

5.8	Protection against penetration of dust & water

5.8.1	The complete meter i.e. case & terminal block shall meet the requirements of IEC-60529 (latest 	edition).  For protection against penetration of dust & water the meter shall be IP54 compliant.

6.0	Electrical Requirements

6.1	Standard Ratings (HT Type Meter)

Rated/Max Current			5/10 Amp

Reference Voltage 			3x63.5/110V

3x57.73/100V

Meter voltages shall be programmable upto 110 volts.

Reference Frequency 			50 Hz

Accuracy Class for kwh			0.5S

Accuracy Class for kvarh		2

Meter Type 	HT type PT & CT operated meters capable to be programmed both for 3-Phase, 3-Wire, 2-Elements OR 3-Phase, 4-Wire 3-Elements system to utilize the same meter according to the system requirement.

6.2	Standard Ratings (LT Type Meter)

Rated/Max Current			5/10 Amp

Reference Voltage 			3x230/400 V

Reference Frequency 			50 Hz

Accuracy Class for kwh			0.5S

Accuracy Class for kvarh		2

Meter Type 	3 Phase, 3 element, 4 wire, for recording true energy in a 4 wire system with neutral solidly grounded

6.3	Other Electrical Requirements

HT		  	LT

Power Losses of voltage 		1.5 W &		1.5 W &

Circuit at reference voltage 		8 VA			8 VA

Current circuit at rated current 		2.5 VA 			2.5 VA

Starting current 				0.001 In at unity power factor with balanced load.

Running with no load 	From 0.8 to 1.15 of reference voltage but with no current Meter shall not produce more than one pulse.

Initial start Up 			Within 5 sec after application of rated voltage

Meter display shall start functioning.

Temperature rise 		25 Degree C with ambient temp.

Of external surface		of 45 Degree C

Temperature rise of 		30 Degree C with ambient temp

Terminal			of 45 Degree C

6.3.1	Dielectric Strength

Power frequency		4 KV for one minute

Withstand voltage

Impulse voltage withstand	 6KV for both HT & LT: 1.2/50 micro sec.

Short time over current		20 times Imax for 0.5 sec.

Insulation resistance 		More than 5 Mega ohms

Creepage Distance 		20 mm Min

6.3.2	Voltage Range

Specified operating			From 0.9 to 1.1 of

Range 					reference voltage

Limit range of operation 		From 0.7 to 1.3 of ref. Voltage

6.4	Accuracy Requirement

Tests and test condition given in IEC 62052-11 (latest edition).

6.4.1	Limits of error due to variation of the current (kwh)

When the meter is under the reference conditions given in 8.1 of IEC 62053-22 (latest edition), the percentage errors shall not exceed the limits for the relevant accuracy class given in Table I and II below.

If the meter is designed for the measurement of energy in both directions, the values in IEC 62053-22 (latest edition) shall apply for each direction.

Table – I

Percentage error limits with balanced loads

| Value of Current | Power Factor | Percentage error Limits for meters of class 0.5S |
| --- | --- | --- |
| 0.01 In < I < 0.05 In | 1 | +1.0 |
| 0.05 In < I < Imax | 1 | +0.5 |
| 0.02 In < I < 0.1 In | 0.5 inductive 0.8 capacitive | +1.0 +1.0 |
| 0.1 In < I < Imax | 0.5 inductive 0.8 capacitive | +0.6 +0.6 |
| 0.1 In < I < Imax | 0.25 inductive 0.5 capacitive | +1.0 +1.0 |

Table – II

Percentage error Limits

(Meter carrying a single phase load but with balanced three-phase voltage applied to the Voltage circuits)

| Value of Current | Power-Factor of the relevant element | Percentage Error Limits for meters of class 0.5S |
| --- | --- | --- |
| 0.05 I <I < Imax. | 1 | + 0.6 |
| 0.1 In < I < Imax | 0.5 inductive | + 1.0 |

The difference between the percentage error when the meter is carrying a single phase load and a 	balanced poly phase load at rated current In and unity power factor, shall not exceed 1.0% for meter 	of class 0.5S.

6.5 	Influence of Other Quantities (kwh)

6.5.1	The additional percentage error due to the change of influence quantities with respect to reference 	conditions, as given in IEC 62053-22 (latest edition), shall not exceed the limits given in Table-	III 	below.

Table – III

Influence Quantities

| Influence Quantity | Value of current (balanced unless otherwise stated) | Power Factor | Mean temperature coefficient %K for meter of class 0.5S |
| --- | --- | --- | --- |
| Ambient temperature variation 9) | 0.05 In < I < Imax 0.1 In < I < Imax | 1 0.5 inductive | 0.03 0.05 |
| - | - | - | Limits of variation in percentage error for meter of class 0.5S |
| Voltage variation + 10% | 0.05 In < I < Imax 0.1 In < I < Imax | 1 0.5 inductive | 0.2 0.4 |
| Frequency variation + 2% | 0.05 In < I < Imax 0.1 In < I < Imax | 1 0.5 inductive | 0.2 0.2 |
| Reversed Phase sequence | 0.1 In | 1 | 0.1 |
| Voltage unbalance | In | 1 | 1.0 |
| Auxiliary voltage ± 15% | 0.01 In | 1 | 0.1 |
| Harmonic components in the current & voltage circuits | 0.5 Imax | 1 | 0.5 |
| Sub harmonics in the a.c. current circuit | 0.5 In | 1 | 1.5 |
| Continuous magnetic Induction of external Origin | In | 1 | 2.0 |
| Magnetic induction of external origin 0.5 mT | In | 1 | 1.0 |
| Electromagnetic RF Fields | In | 1 | 2.0 |
| Operation of accessories | 0.01 In | 1 | 0.1 |
| Conducted disturbances, induced by radio-frequency fields | In | 1 | 2.0 |
| Fast transient burst | In | 1 | 2.0 |
| Damped oscillatory waves immunity | In | 1 | 2.0 |

    - For the voltage ranges from – 20% to - 10% and + 10% to +15% the limits of variation in %age errors are three times the values given in table - III.

    - The distortion factor of the voltage shall be less than 1%.

    - The variation in %age error shall be measured under the most unfavorable phase displacement of the third harmonic in the current compared with the fundamental current.

    - Three-phase meters shall measure and register within the limits of variation in %age error shown in Table-III if one or two phases of the 3-phase network are interrupted

    - The test conditions are specified in relevant latest IEC.

    - A magnetic induction of external origin of 0.5 mT produced by a current of the same frequency as that of the voltage applied to the meter and under the most unfavorable conditions of phase and direction shall not cause a variation in the percentage error of the meter exceeding the value shown in the Table-III.  The test conditions are specified in relevant latest IEC.

    - The Test conditions are specified in relevant latest IEC.

    - Such an accessory, when enclosed in the meter case, is energized intermittently, for example the Electro-magnet of a multi rate register.

    - It is preferable that the connection to the auxiliary device(s) is marked to indicate the correct method of connection.  If these connections are made by means of plugs and sockets, they should be irreversible.

    - Limits of error due to ambient temperature variation.

The mean temperature coefficient shall not exceed the limits given in Table – IV.

Table – IV

##### Temperature Coefficient

| Value of current | Power Factor | Mean Temp. coefficient % IK for meters of class 0.5S |
| --- | --- | --- |
| 0.05 In < I < Imax | 1 | 0.03 |
| 0.1 In < I < Imax | 0.5 inductive | 0.05 |

6.6	Limits of Error Due to Variation of the Currents (kvarh)

6.6.1	When the meter is under reference conditions given in IEC 62053-23 (latest edition). The 	percentage errors shall not exceed the limits given in Table V & VI.

Table – V

Percentage error limits with balanced loads

| Value of Current | Sin  (Inductive or Capacitive) | Percentage error limits for meter of Class-2 |
| --- | --- | --- |
| 0.05 Ib < I <0.1 Ib | 1 | +2.5 |
| 0.1 Ib < I < Imax | 1 | +2.0 |
| 0.1 Ib < I <0.2 Ib | 0.5 | +2.5 |
| 0.2 Ib < I < Imax | 0.5 | +2.0 |
| 0.2 Ib < I < Imax | 0.25 | +2.5 |

Table – VI

Percentage error limits (poly-phase meter carrying a single phase load but with balanced            	poly-phase voltages applied to the voltage circuits).

| Value of Current | Sin  (Inductive or capacitive) | Percentage error limits for meter of Class-2 |
| --- | --- | --- |
| 0.1 Ib < I < I max | 1 | + 3.0 |
| 0.2 Ib < I < I max | 0.5 | + 3.0 |

The difference between the percentage error when the meter is carrying a single phase load 	and a balanced poly phase load at basic current Ib and sin  = 1 shall not exceed 2.5%.

The energy for inductive load be recorded and should register the absolute some of quadrant           	1 & 3.

6.7	Limits of Error Due to Influence Quantities (kvarh):

6.7.1	The additional percentage error due to the change of influence quantities with respect to reference 	conditions, as given in IEC 62053-23 (latest edition) shall not exceed the limits given in         	Table-VII.

### Table-VII

Influence Quantities

| Influence quantity | Value of Current (balanced unless otherwise stated) | Sin  (Inductive or capacitive) | Mean temperature coefficient % K for Meters of class 2 |
| --- | --- | --- | --- |
| Ambient temperature Variation | 0.1 Ib < I < I max 0.2 Ib < I < I max | 1 0.5 | 0.10 0.15 |
|  |  |  | Limits of variation in Percentage error for Meters of class 2 |
| Voltage variation +10% | 0.05 Ib < I < I max 0.1 Ib < I < I max | 1 0.5 | 1.0 1.5 |
| Frequency variation +2% | 0.05 Ib < I < I max 0.1 Ib < I < I max | 1 0.5 | 2.5 2.5 |
| DC component in the current circuit | Imax 2 | 1 | 6.0 |
| Continuous magnetic induction of external origin | Ib | 1 | 3.0 |
| Magnetic induction of external origin 0.5 mT | Ib | 1 | 3.0 |
| Electromagnetic RF Fields | Ib | 1 | 3.0 |
| Operation of accessories | 0.05 Ib | 1 | 1.0 |
| Conducted disturbances, induced by radio-frequency fields | Ib | 1 | 3.0 |
| Fast Transient burst | Ib | 1 | 4.0 |

i)	For the voltage ranges from –20% to 10% and +10% to +15%, the limits of variation in percentage 	errors are three times the values given in this Table-VII.

Below 0.8 Un the error of the meter may vary between +10% and -100%.

ii)	The recommended point for voltage variation and frequency variation is Ib for direct connected meters.

iii)	The purpose of this test is to check for current sensor saturation only.

iv)	The test conditions are specified in IEC 62053-23 (latest edition).

v)	A magnetic induction of external origin of 0.5 mT produced by a current of the same frequency as that of the voltage applied to the meter and under the most unfavorable conditions of phase and direction shall not cause a variation in the percentage error of the meter exceeding the values shown in this Table.

The magnetic induction shall be obtained by placing the meter in the centre of a circular coil, 1 m in mean diameter, of square section and of small radial thickness relative to the diameter, and having 400 At.

vi)	Such an accessory, when enclosed in the meter case, is energized intermittently, for example the 	electromagnet of a multi rate register.

It is preferable that the connection to the auxiliary device(s) is marked to 	indicate the correct method 	of connection. If these connections are made by means of plugs and sockets, they should not be 	interchangeable.

The mean temperature coefficient shall be determined for the whole operating range. The 	operating 	temperature range shall be divided into 20 K wide ranges. The mean temperature 	coefficient shall 	then be determined for these ranges, by taking measurements 10 K above and 10 	K below the 	middle of the range. During the test, the temperature shall be in no case outside the specified 	operating temperature range.

6.8	Meter Constant

The relation between the test output and the indication in the display shall comply with the marking on the nameplate.

Output devices generally do not produce homogeneous pulse sequence.  Therefore, the manufacturer shall state the necessary number of pulses to ensure a measuring accuracy of at least 1/10 of the class of the meter at the different test points.

7.0	Meter Characteristics

The meter shall generally comprise of the following characteristics as a minimum. A list of characteristics of appended below divided in seven parts:

7.1	Basic Data Recording & Storage.

    - Min. Four TOD periods Energies (KWH)

    - Min. Four TOD periods Energies (KVARH).

    - Min. Four TOD periods Max. Demand (KW).

    - Min. Four TOD periods Max. Demand History (KW).

    - Min. Four TOD periods Cumulative Max. Demand (KW).

    - No. of Resets along with Data and Time Stamp for Last Reset.

    - Present interval Demand.

    - Time left in interval.

    - Average Power Factor, continuous and by rate.

    - Last Twelve (12) months Billing Data KWH, KVARH, KW continuous & by rate shall be available at all times.

  - End of Billing Period

    - Historical registers store a copy of energy overall registers and maximum demand registers information at the end of the billing period.  The information must be retained in a circular buffer (Last In / Last Out) for 16 billing periods.

    - A billing period is defined as the period between 2 successive maximum demand resets.

    - The reset of maximum demand must be determined by any of the following ways:

- Automatically on pre-defined dates.

- By an input signal.

- By remote communication interface command or by communication with an optical head.

- Automatically according a defined date, which was downloaded since the last reset by remote communication

- The meter must be designed and manufactured in such way to foresee protection from accidental MDI reset with programmable time delay (in minutes).

7.3	Security Features, Event Recording, & Diagnostics:

    - Security Features.

- Every Meter shall have a unique serial no. in its memory which can be displayed / reported.

- The No. of times programmed and the identification of the last programmer along with Date & Time stamp shall be reported/displayed

- A programmable meter ID code shall be provided.

- At-least two levels of access/security codes shall be provided one for meter reading (only) by the authorized personnel and a second one for programming and reading.

- Meter shall keep on recording/operating as long as any voltage exists with or without neutral connected.

- No data entry keys / push buttons shall be provided in the meter for any manual programming.

- The meter shall be protected against any loss of data and functional performance due to any external interference such as influence of Strong/Radar Magnet, CD drive, Mobile phones and shall comply to all relevant IEC/ANSI standards.

    - Security Logging with Date and Time Stamp.

- Total No. of Power Outages.

- Phase failure and Disconnection of wires excluding neutral wire

- Reverse energy flow

- Reverse Polarity

- At-least 100 total events shall be recorded in the meter at any one time before Roll Over they may comprise of the above or any additional features.

- Optical Port Communication with Date and Time Stamp.

7.3.3	Diagnostics

The meter shall display cautions and diagnostics for the following conditions.

- a)   Demand Overload Warning.

- Over and under Voltage (with Date & Time Stamp). The over and under voltage should be programmable.

- By –passing the incoming energy, current and voltage quantities (with Data & Time Stamp).

- Un-programmed Meter.

- Self check diagnostics for RAM/ROM, Processor, non-volatile memory failure and other essential hardware circuitry.

7.4 (a) Display

a)   	The Display shall be LCD type with at-least eight (08) whole digits without decimal for 	Energy consumption.

- b) 	Maximum demand shall have at least three whole digits and two decimal digits.

- c)	Display scrolling time shall be programmable.

- d)  	Min. three programmable display modes shall be available.

e)	One Display mode shall be the normal or automatic display mode.  Other display mode 	shall be for security / diagnostics etc and the third display mode shall be for test purposes.  	Activation of display mode shall be with a push button.

- The battery shall be able to display all the quantities selected for normal mode display 	during power outage through push button.

- Phase indicators.

- Power quadrant indicator.

- All segment check.

- Active TOD period indicator.

- Display mode indicator.

- Display quantity labels.

- Pulse output for field testing of meter shall be available on the display / optical interface.

n) 	I/O interface (optional), data retrieval in case of power OFF (optional).

7.4. (b)	Scroll Display

It shall be suitable to measure in all four quadrants and display the following electrical quantities for 3 Phase load: -

- LCD segment to check display.

- Date.

- Real time.

- Instantaneous Frequency.

- Active Energy (KWH) Peak + off Peak.

- Reactive Energy (KVARH), Peak + off Peak.

- Maximum demand (KW).

- Cumulative Maximum demand (KW).

- MDI resets count (Numbers).

- Instantaneous Power (KW).

- Instantaneous average Power Factor (Lagging/Leading).

- Instantaneous three phase voltages (Phase wise).

- Instantaneous Phase wise line currents.

- Current transformer ratio.

- Voltage transformer ratio.

- Status word operated indication with date

- The electronic register shall have non-volatile memory to retain data during power outages for at least 10 years.  The operation of electronic module and contents of the register shall not be affected by external magnetic field/electromagnetic pulses and radio frequency signals.

- The electronic register display shall be of liquid crystal type.  The figures shall be of sufficient size to facilitate reading from a distance of at least 4 feet.  The sequence of display shall be clearly indicated on the name/rating plate of the meter.

- The meter shall perform self-diagnostic operation continuously to identify errors automatically about low battery voltage, loss of program and data errors, etc.

- The meter shall show the following information on a clearly visible display.

- An indication of consumption on each phase to show on the front panel, (flashing indicator, etc).  The absence of consumption to be indicated by a static indicator, and absence of voltage on any phase to be shown by the indicator being switched off.

- In the case of automatic MDI reset operation, the meter shall give an indication of whether the meter cover has been opened.

- Various instantaneous quantities e.g. phase-wise voltages, current, power factor and load (KW) shall be obtainable from a data collection device.

- The solid state energy meter shall have the provision to display all parameters in the following modes:

- Auto-display.

- Manual scroll.

- Fast scroll.

- Scroll both forward and backward direction.

Scroll lock shall be available to get display of any one parameter continuously by pressing push button.

7.5.	Load Profiling / Recording

7.5.1	Min. Two Channel recording-having sufficient capacities to record at-least 65 days of Data of 30 	minutes interval

7.5.2 Load Profile Data shall also be downloadable in the meter reporting software for future 	processing.

7.5.3     All Load Profile Data shall be stored in a Non-Volatile Memory.

7.5.4     Load profile interval length should be programmable.

7.6.	Back-up Battery

7.6.1	The backup Battery shall be of Lithium-ion type.

7.6.2	Low Battery indication shall be displayed when min. 25% battery life is left.

7.6.3	Storage life of Battery shall be more than 15 years.

7.6.4 	Without any Power, the Back-up battery shall maintain display ON by push button (optional) and 	the time, calendar TOD program for a continuous period of at-least for three years.

7.6.5 	The battery shall be solidly welded inside the main cover. However, if battery is provided 	outside the main cover then it must have separate sealing arrangement.

7.7.	Meter Programming, Software, & Security

The following features shall be programmable in the meter as a minimum along-with other features that may be provided:

    - Meter Reading Multiplier.

    - Demand Time interval (1, 10, 15, 30, 60 minutes).

    - Annual Calendar Programmable for Four seasons, Four Tariffs/Rates daily, min. 100 programmable dates/days to account for holidays and weekends.

    - The meter shall have upgradeability option both in Hardware and Software to configure for other ancillary devices.

    - Demand resets can be configured for automatic resets on a preset date to override the manual reset.

    - The meter shall be Multi Vendor compliant.

    - Meter should be DLMS/COSEM complaint or IEC-62056-21 (Former IEC1107) compliant.

    - Meter programming shall be Windows bases.

    - Optical Communication Port of the meter shall either be IEC 1107 (latest edition).

    - The meter shall have non-volatile EPROM memory.

    - Once programmed the meter shall be re-programmable as a new meter with all previous readings of KWH, KVARH, KW to be made zero through the required security passwords.

    - The manual button can be disabled.

7.8.	Reporting Software, Security & Anti – Tampering Features.

Safety Levels.

    - Access to the meter will be determined by four (4) levels of access according to IEC-61107 (latest edition) and there will also be extra special levels of safety which are determined by the user.  The access levels will be as follows:

-	Level 0  :  Access without prerequisites.

- -	Level 1  :  Access only with a code without codification.

- -	Level 2  :  Access with a code with codification.

-	Level 3  :  Access only after removing the control seal and pressing of the button.

    - The safety levels will be hierarchically structured which means that access to a particular level means access to all the levels below it.

The different data and/or data groups are registered to a particular safety level according to IEC-61107 (latest edition).

- -	The Software shall be password protected.

-	The Reporting software shall be windows based and have the connectivity with computer through USB port.

- -	It shall be possible to graphically represent Load Profile Data reports.

-           It shall be possible to convert all reports to PDF & Excel format.

7.8.3	Unauthorized Access and Tampering:

Additionally, the diagnostic system, meter monitors continuously for unauthorized tampering of 	the meter.  The following disturbances are tagged and can be recorded.

-	Each opening of the meter.

-	Disconnection of wires.

-	Sudden un-balances of currents.

-	Power outages per phase.

-	The meter should communicate “Total power break down” event as soon as it occurs. Back up battery or super capacitor may be used for this communication.(optional)

·      -	The meter should be capable of recording terminal cover opening event & main cover opening event even during total breakdown condition. The same may be communicated immediately or recorded and communicated when power is ON.(optional)

7.8.4	Modem

Modems must be pluggable type or built in and should be completely protected by the terminal cover or inside the main cover of the meter.

The modem shall  be auto-supplied by the meter itself.

The modem must have standard interface.

The modem shall initiate a message/notification in the event of any tamper being logged by the meter and shall be able to send the relevant data to the AMM system immediately such as:

- Inactive phase current.

- Voltage phase deviation.

- Inactive phase.

- Energy polarity current.

Modem must be easily configurable through modem software and modem software must be in English language.

The modem must be accessible remotely  by standard  commands or by meter software or modem software and must be password protected. Modem must be capable to report signal strength remotely over meter software or modem software.

    - Antenna

A powerful built-in antenna shall be provided inside the main cover. However, in addition, option for connecting outdoor antenna shall be available inside terminal cover or outside terminal cover within ATB.

    - Software & Demonstration

The bidders who have participated in the tender shall arrange meter software features and AMR demonstration of their offered meters in KESC’s Meter Testing Lab in presence of R&D, Meter Department, AMS Department and SAP-EDM representatives.

    - Remote software/firmware upgradation;

Meter should be capable of upgrading software /firmware through remote connection.

7.8.8	Meter Programming Software

The successful bidder shall provide the meter programming software free of cost for programming the AMR meters.

8.0	Tests

Following routine, type and sample tests shall be carried out as per requirements of IEC-62052-11 and other relevant IECs (latest edition)

8.1	Routine Tests

Following routine tests shall be carried out on solid state meters as per respective IEC:

    - Accuracy Test.

    - Running with no load test.

    - Starting current test.

    - Insulation resistance test

8.2	Type Test

Type test shall be carried out on AMR solid state energy meters at an independent accredited 	laboratory like KEMA of Holland, CESI Italy, CRIEPT Japan or HV&SC laboratory Rawat, 	Islamabad Pakistan. The tests shall be carried out at independent Laboratory criteria of selection of 	samples and acceptance / rejection shall be as per relevant IEC.

8.2.1	Tests of Mechanical Requirements

- a)	Spring hammer test.

- b)	Shock test.

- c)	Vibration test.

- d)	Test of resistance to heat and fire.

- e)	Test of protection against penetration of dust and water.

8.2.2	Test of Climatic Influence

- Dry heat test.

- Cold test.

- Damp heat cyclic test.

- Solar radiation test.

8.2.3	Tests of Electrical Requirements

- a)	Test of power consumption of voltage circuits.

- b)	Test of power consumption of current circuits.

- c)	Test of effect of voltage dips and short interruptions.

- d)	Test of influence of short time over-current.

- e)	Test of influence of self-heating.

- f)	Test of influence of heating.

- g)	Impulse voltage test.

- h)	A.C. voltage test.

    - Test of Electromagnetic Compatibility (EMC)

The meter shall be tested in accordance with the following IECs (latest editions):

- Electrostatic discharge according to IEC 61000-42.

- Electromagnetic HF fields according to IEC 61000-4-4.

- Transmission line transient s according to IEC 61000-4-4.

- Attenuation of radio interference according to IEC/CISPR22 class-B.

    - Tests of Accuracy requirements (for KWH meter parts as per IEC 62053-22 (latest edition) & for KVARH meter IEC-62053-23 (latest edition) where applicable.

a)   Test of Accuracy.

- b)   Test of influence quantities.

- c)   Test of ambient temperature influence.

- d)   Test of no load condition.

- e)   Test of starting condition.

9.0	Name & Rating Plate

9.1	A suitable name/rating plate of anodize aluminum shall be provided inside at the front of the meter indicating the following engraved/printed information:

- 9.1.1	Name of the manufacturer and country of origin.

- 9.1.2	Type of meter.

- 9.1.3	Nominal and maximum current, nominal voltage and frequency.

- 9.1.4	Important display sequence with codes.

- 9.1.5	KESC Purchase Order No.

- 9.1.6	Works Serial No. and year of manufacture.

- 9.1.7	Property of KESC, not for sale.

- 9.1.8	SAP item code no.

- Packing

The meter shall be suitably packed by the supplier to ensure safe delivery at the destination.

  - Each meter shall be individually packed in thermo pore packing or thermo pore lined packing, covered with adhesive tape at joints or plastic strips etc.

10.2.	For overseas shipment, a suitable number of individually thermo pore packed meters shall then further be packed in seaworthy packing.

10.3.   The packing shall be strong enough to withstand rigors of ocean, rail, road etc.

11.0	Sample

All participants to the bid should submit – along with their offer at least 2 (two) complete samples of each offered item as to facilitate the materials evaluation.  Offers which are not accompanied by samples will not be accepted.

12.0	Inspection

The successful bidder shall offer the meters for testing/inspection.  Procedure for pre-shipment inspection is given below:

12.1	Sample Tests (Electrical)

    - The meters offered for acceptance shall be grouped into lots containing up to 100 meters.  A sample comprising of five (05) meters shall be selected at random from each lot and subjected to tests as below:

-    	Starting Current.

-    	Creep Test.

-    	Accuracy Test.

-    	A.C. Voltage Test.

12.1.2	The meters offered for acceptance shall be grouped into lots containing up to 100 meters. A sampled comprising of two (02) meters shall be selected at random from each lot and subjected to following tests:

- 	Impulse test.

-    	Power loss test.

12.1.3	The lot shall be accepted if all the meters qualify in the tests described in clause 12.1.1 & 12.1.2 above.  The lot shall be rejected if two or more meters fail in any of the tests.  If any one-meter fails in any of the above tests re-sampling shall be carried out after collecting same no. of meters and subjected to the tests described in clause 12.1.1 & 12.1.2 above.   If any one-meter fails in any of the above tests the whole lot shall be rejected.

12.2	Sample Tests (Mechanical)

    - The meter offered for acceptance shall be grouped in to lots containing up to 100 meters.   Sample comprising of three (03) meters shall be selected at random from each lot and subjected to tests as below:

Sr. No.		Description					Nos. of Meters

i) 		Test of protection against penetration

of dust and water				One meter

ii)		Dimensional Check				One meter

iii)		Tests for Electromagnetic Interference (EMI)	One meter

The lot shall be accepted if meters qualify the above tests in clause 12.2.1.  In case any meter fails in the relevant test, another sample of double the quantity shall be selected and test/tests repeated.  If any meter fails in the relevant test in the second group, the entire lot shall be rejected.

12.3	Verification Test of Functionality of Software

12.3.1	Verification test of the functionality of software and display features on offered meters shall be performed by loading/unloading of programmed and auditing the diagnostic reports.  The number of meters shall be three.  If any meter fails to comply with the functionality requirements the entire offered lot shall be rejected.

12.3.2	The remaining type tests not performed on the above samples shall be carried out (as per recommended sequence of IEC-62052-11 Annexure-F) on three (03) Nos. meters out of the total offered meters.  If two meters fail in any of the above tests, the lot shall be rejected.  If one of the meters fails to qualify any of the above tests, re-sampling shall be carried out.  In case of failure of any meter in any of the tests the lot shall be rejected.

13.0	Warranty.

The supplier shall provide two years warranty for the successful operation of the meter including its maintenance whenever required. Any change suggested by the user/evaluation committee in the reporting software shall be accommodated. The defective meters shall be replaced with new ones free of cost within warranty period.

14.0	Training

The successful bidder shall arrange comprehensive practical training regarding, trouble-shooting programming, billing, loading of software etc. at manufacturer works or in KESC on his own cost.

15.0	Bid Data, Test Certificates, Drawings, Literature, Reference List & Manufacturing Experience

All the bidders shall submit complete technical data, detailed drawings test certificates, literature in English language, supply reference list and manufacturing experience along with the bid.

The following should accompany the bid:

- i)	Constructional drawing indicating the dimensions of the meters.

- ii)	Detailed description of the meter.

- iii)	Constructional and test regulations as well as their Test certificates.

- iv)	Certificate of ISO 9001 or 9002 for the factory standards.

v)	Meter’s connection in 3-phase 4-wires (3-Elements meter) network by current transformer.

vi)	Meter’s connection in 3-phase 3-wires (2-Elements meter) network by current transformer.

vii)	Diagram for signal processing.

viii)	Schematic diagram for the Energy registers.

16.0	Operation Instructions

The bidders must deliver with their offers a copy of the operation manual and the supplier must deliver 10 copies of the above manual during the first delivery.

17.0	Manuals for Maintenance & Repair

The bidders must deliver with their offer manuals for maintenance and repair including instructions for check and regulation and the necessary software.

Additionally the supplier must deliver troubleshooting list with the method “step by step” and diagrams of the internal wiring within 15 days from the signature of the contract.

18.0	Possibilities for Acceptance / Rejection of Bid

KESC retains the right to accept or reject offers which are not in accordance with one or more requirements of this technical specification. Similarly KESC may consider offers where exceptions are highlighted by the vender if it feels these exceptions may be considered acceptable in certain circumstances.

19.0	Disclaimer

The subject specification(Annex II) are according to current AMM/communication systems and 	would be modified accordingly if any change will occur in AMM/communication systems.

Reference Standards (Annexure-1)

When following standards referred to in this document have been superseded, the latest revisions shall apply.

(01)	Metering Standards

62052-11: 		Electricity metering equipment (AC).

(latest edition)		General requirements, tests and test conditions Part-11: Metering equipments.

62053-22		Electricity metering equipment (AC).

(latest edition)		Particular requirements Part-22: Static meters for active energy                              				(clauses 0.2S & 0.5S).

62053-23		Electricity metering equipment (AC).

(latest edition)		Particular requirements Part-23: Static meters for reactive energy (clauses 2 & 3).

IEC 529		Degrees of protection provided by enclosures

(latest edition)

IEC 1334-4-41		Distribution automation using distribution line carrier

(latest edition)		systems – Part 4 : Data communication protocols – Distribution line message

Specification.

IEC 62056-21       	Electricity metering – data exchange for meter reading, tariff and load control –

(latest edition)	            Part 21: Direct local data exchange.

IEC 62056-53		DLMS/COSEM Application Layer

(latest edition)

IEC 62056-61		DLMS/COSEM OBIS Code

(latest edition)

IEC 62056-62		DLMS/COSEM Interface Classes

(latest edition)

#### IEC 62056-72		DLMS/COSEM Data Link Layer

(latest edition)

IEC 61107		Data exchange for meter reading, tariff and load control

(latest edition)

IEC 1038		Electricity metering – Tariff control

(latest edition)

IEC 410		Sampling plans and procedures for inspection by attributes

(latest edition)

IEC 68-2-6		Basic environmental testing Procedures Part 2: Tests Test EA : shock

(latest edition)

IEC 68-2-30		Basic environmental testing Procedures Part 2: Tests. Test Db: Damp, neat cyclic (latest edition)	 	(12 + 12 – hour cycle)

IEC 695-2-1		Fire hazard testing part 2: Test methods Glow wire test

(latest edition)

IEC 695-2-2		Fire hazard testing part 2: Test methods Needle flame test

(latest edition)

(02) 	Electrical Testing Standards:

60038:			IEC standard voltages.

(latest edition)		50(301,302,303): 1983, International Electro technical vocabulary (IEV)

Chapter 301: General terms on measurements in electricity.

Chapter 302: Electrical measuring instruments. Chapter 303: Electronic measuring 			instruments.

60060,			High voltage test techniques

(latest edition)

60085: 			Thermal evaluation and classification of electrical insulation.

(latest edition)

60664: 			Insulation co-ordination within low voltage systems including clearance and

(latest edition)		creepage distances for equipment.

60736: 			Testing equipment for electrical energy meters

(latest edition)

60801-2: 		Electromagnetic compatibility for industrial-process

(latest edition)		measurement and control equipment. Part-2: Electrostatic discharge requirements.

60801-3		Electromagnetic compatibility for industrial process measurement and control

(latest edition)		equipment.  Part-3: Radiated electromagnetic field requirements.

60801-3: 		Electromagnetic compatibility for industrial-process measurement and control

(latest edition)		equipment. Part-4: Electrical fast transient/burst requirements.

CISPR14: 		Limits and methods of measurement of radio interference characteristics of

(latest edition)		household electrical appliances, portable tools and similar electrical apparatus.

(03).	Mechanical Testing Standards

60529:			Degrees of protection provided by enclosures (IP code)

(latest edition)

60695-2-1:		Fire hazard testing, Part-2: Test methods Glow-wire test and guidance

(latest edition)

60817: 			Spring operated impact test apparatus and its calibration.

(latest edition)

(04)	Environmental Standards

60068-2-1:		Environmental testing, part2: Tests. Tests A: Cold

(latest edition)

60068-2-2:		Environmental testing, part2: Tests. Tests B: Dry Heal

(latest edition)

60068-2-5:		Environmental testing, part2: Tests. Test Sa: Simulated solar radiation at ground

(latest edition)		level.

60068-2-6:		Environmental testing, part2: Tests. Test Fc and guidance: Vibration (sinusoidal).

(latest edition)

60068-2-11:		Environmental testing, part2: Tests. Test Ka: Salt mist

(latest edition)

60068-2-27:		Environmental testing, part2: Tests. Test Dd and guidance: Damp heat, cyclic (12 +

(latest edition)		12-hour cycle)

60721-1:Ed.2.0.b,	Classification of environmental conditions. Part 1: Environmental parameters and

(latest edition)		their severities.

60721-2-1:		Classification of environmental conditions. Part 2: Environmental conditions

(latest edition)		appearing in nature. Temperature and humidity

60721-2-4:	 	Classification of environmental conditions. Part2: Environmental conditions

(latest edition)		appearing in nature. Solar Radiation and temperature

| Technical data sheet LT/HT CTO meter |  |  |
| --- | --- | --- |
|  | K/R&D/SMCTO/01 |  |
| S/# | Description | Offered Values |
| a | Manufacturer's Name & Origin |  |
| b | Manufacturing Experience |  |
| c | Quantity / Price with GST |  |
| 1 | Model No./Type |  |
| 2 | Rated current |  |
| 3 | Maximum current |  |
| 4 | Minimum starting current at ref. |  |
|  | Voltage & ref. Frequency |  |
| 5 | Operating voltage |  |
| 6 | Overload capacity |  |
| 7 | Accuracy Class |  |
| 8 | No. of elements |  |
| 9 | Losses in |  |
| I). | Potential circuit |  |
| ii). | Current circuit |  |
| 10 | Max. current that meter can withstand during short circuit for 0.5 second. |  |
| 11 | Dielectric strength |  |
| I). | Impulse Voltage |  |
| ii). | A.C. test voltage |  |
| 12 | Insulation resistance of meter |  |
| 13 | Material of: |  |
| a). | Base |  |
| b). | Main Cover |  |
| c). | Terminal Block |  |
| d). | Terminal Cover |  |
| 14 | Temperature rise of meter |  |
| 15 | Type of terminals |  |
| 16 | Centre to centre clearance -between different phases |  |
| 17 | Whether the meter is complaint to the reference standard for the testing mentioned in the specs. |  |
| 18 | Whether the meter have the following characteristics. |  |
| a | Basic data recording and storage (as per clause 7.1 of the spec.) give details. |  |
| b | Security features, Events recording and Diagnostics; (as per clause 7.3 of the spec.) give details especially. |  |
| I). | Meter records with or without neutral Connected. |  |
| ii). | Logging of by-passing incoming energy. |  |
| c). | Display. (as per clause 7.4 of the spec) give details. |  |
| d). | Load profiling/recording. (as per clause 7.5 of the spec) give details. |  |
| e). | Back-up Battery. (as per clause 7.6 of the spec) give details. |  |
| f). | Meter Programming, Software and security;(as per Clause 7.7 of the spec) Give details. |  |
| g). | Reporting Software & security (as per clause 7.8 of the spec) give details. |  |
| 19 | Operating ambient temp. range |  |
| 20 | Size & No. of digit of LCD Display |  |
| 21 | Whether meter have the upgrade-ability option |  |
| 22 | What is sampling rate |  |
| 23 | Impulse test voltage with energy |  |
| 24 | I.P. class of meter |  |
| 25 | No. of digit of following features: |  |
| I). | KWH |  |
| ii). | KVARH |  |
| iii). | Demand KW |  |
| iv). | Cumulative KW |  |
| v). | No. of Reset digits |  |
| 26 | What values/readings are controlled through resetting device? |  |
| 27 | Detail of resetting device with sealing arrangement (give drawings) |  |
| 28 | Min No. of tariff/rates for which the Tariff register can be programmable for: |  |
| - | KWH |  |
| - | KVARH |  |
| - | KW |  |
| 29 | Effect of external magnetic field/pulses on meter |  |
| 30 | Effect of Radio frequency signals |  |
| 31 | Type of memory |  |
| 32 | Storage capacity of memory |  |
| 33 | Time of retain the memory |  |
| 34 | Detail of push button/other mechanism for reading different values of register. |  |
| 35 | In case of error in register which types of checks are provided which automatically identifies the error. |  |
| 36 | Meter Clock |  |
| a). | Source of operation of built in clock |  |
| b). | Effect of variation of frequency of source. |  |
| c). | Source of operation of clock in case of power outage |  |
| d). | If battery is used, what is the life of battery. |  |
| e). | Period/life for which the battery can supply power continuously to check and register prior to its discharge below 25%. |  |
| f). | The timing element is programmable through |  |
| g). | Detail of programming device. In case of handheld programming device group of meter of which one programming device is supplied. |  |
| h). | No. of programmable dates to account for holidays and weekends. |  |
| I). | Behavior of TOD meter during Discharge Battery. |  |
| 37 | Name/rating plate, detail of information given on name plate. |  |
| 38 | Attachments Whether the following material has been attached: |  |
| a). | Accuracy Curves |  |
| b). | Drawing of Meter Showing dimensions, mounting details etc. |  |
| 39 | Bidders/manufacturer have to supply all relevant drawings & technical literature duly marked. |  |
| 40 | Details of deviations of the offered meter from specification (use separate sheet if required). |  |

KESC AMM System (Annexure-II)

KESC AMM (Automated Metering Management) System consists of meter data acquisition and metering data management system that communicates with field devices over VPN based upon GPRS. One of the most important requirements is the compatibility of offered AMR meter with KESC AMM system and SAP ISU billing Engine.

GPRS Modem:

GPRS Modems must be pluggable type or built in and should be completely protected by the terminal cover or inside the main cover of the meter.

The modem shall  be auto-supplied by the meter itself.

The modem must have standard SIM interface.

The modem must support VPN (Virtual Private Network) means that APN could be set.

The modem must support SIMs with static IP

The modem shall initiate a message/notification in the event of any tamper being logged by the meter and shall be able to send the relevant data to the KESC AMM system immediately such as:

- Inactive phase current.

- Voltage phase deviation.

- Inactive phase.

- Energy polarity current.

Modem must be easily configurable through modem software and modem software must be in English language.

The modem must be accessible remotely over VPN by standard telnet commands or by meter software or modem software and must be password protected. Modem must be capable to report signal strength remotely over VPN by telnet commands or meter software or modem software.

Meter Software:

Meter software should be capable to communicate with meter remotely over VPN based upon GPRS as well. Meter software must have the capability to read LPs, meter time, log book and time synchronization over VPN based upon GPRS. Meter software must be capable of parameterization of meter (LP reconfiguration, reprogramming of Tariff, Display, DRO etc.) remotely over VPN based upon GPRS with security passwords.

KESC AMM System Manufacturer: Pre-Requisites:

- The offered AMR meter must be either DLMS/COSEM compliant or IEC 62056-21 (Former 1107) compliant. The following billing/load profile data is required to be fetched by AMM in addition to alarms/events and meter time read/synchronization.

Billing Registers:

ActiveEnergyPlus_CUM_T0,T1,T2

MaximumDemandActivePlus_T0,T1&T2

ReactiveEnergyPlus_CUM_T0,T1&T2

LP1:

Power Registers (A+,A-,R+,R-,S+,S-) with last average

LP2:

Phase currents, phase voltages, phase PFs

- Load profile values (records) must have associated status codes for automatic billing by SAP ISU billing engine. Status codes for load profile records are required against following events at minimum.

Measuring device error

Measuring device battery discharged

Periodic or manual reset of billing values

Summer/winter time or winter/summer time change

Longer measurement period, time synchronization

Shorter measurement period, time synchronization

Power restored during measurement period

Power failure during measurement period

Valid Value

Each status code will be Hex sum of all events associated to the corresponding record.

Sample Load Profile with Status Codes:

| Time | Status | A+ [kW] | A- [kW] | R+ [kvar] | R- [kvar] | S+ [kVA] | S- [kVA] |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1/6/2012 14:00:00 | 00000000 | 98 | 0 | 17.2 | 0 | 99.6 | 0 |
| 1/6/2012 14:30:00 | 00000000 | 213.2 | 0 | 44.8 | 0 | 218.8 | 0 |
| 1/6/2012 15:00:00 | 000000C0, Power down, Power up | 34.4 | 0 | 17.2 | 0 | 44 | 0 |
| 1/6/2012 15:30:00 | 00000080, Power down | 12 | 0 | 6.4 | 0 | 14.4 | 0 |
| 1/6/2012 17:30:00 | 00000040, Power up | 0 | 0 | 0 | 0 | 0 | 0 |
| 1/6/2012 18:00:00 | 00000000 | 155.6 | 0 | 35.2 | 0 | 160.4 | 0 |
| 1/6/2012 18:30:00 | 00000000 | 165.2 | 0 | 40.8 | 0 | 170.4 | 0 |

Integration of 3rd Party Meter with KESC AMM System:

The following functionality of meters would be implemented into AMM System.

- Data reading (Indexes, LP) along with LP status codes
-  Events’ Log reading
-  Alarm functionality

-  Translation of LP status codes of meters into AMM codes
- Meter time read and synchronization

Meter Manufacturer will have to provide the following items but not limited to:

- Two samples of each meter type to be integrated

- Specifications of communication protocol of IEC 62056-21 or DLMS/COSEM which ever meter supports

- Description of object implementation along with event enumeration