Index

- Specs No. K/R&D/264 Rev (00).                	dated                24th Dec, 2012

Specification for Three Phase Direct Online AMR TOU Static Energy Meters    5 KW & Above (Accuracy Class-1)

- Foreword

  - This specification has been prepared by Research & Development Department.

  - This Specification is intended for the purpose of technical specification only for the procurement of material and does not include provisions of contract, unless otherwise provided in the contract.

  - This Specification is subject to revision as and when required.

1.0	Scope

1.1	The specification covers static poly-phase AMR energy meters with modem capable of measuring MDI-kW, kWh & kvarh, along with other quantities and built-in programmable features mentioned in this specification.

Integration means successful data polling (load profile data, Energy Registers, Time Synchronization and events/alarms data) by AMM system.

1.2	This specification covers:

3-phase, 4 wire, 3 element, 3x230/400 V, 10/100 Amp, 50Hz whole current AMR energy meter with communication modem, kWh of Accuracy Class 1 & kvarh of Accuracy Class 2 with multi-rate  function.

2.0	Reference standards

The Reference Standards are listed and provided in Annex – I.

Details of AMM system, billing engine & communication module are provided in Annex-II

3.0	Definitions

3.1	Static watt-hour meter

Meter in which current and voltage act on solid state (electronic) elements to produce on output proportional to watt-hour

  - Measuring element

Part of the meter which produces an output proportional to the energy

  - Test output

Device which can be used for testing the meter

  - Operation indicator

Device which gives a visible signal of the operation of the meter

  - Memory

Element which stores digital information

  - Non-volatile memory

Memory which can retain information in the absence of power

  - Display

Device which displays the content (s) of (a) memory (ies)

  - Register

Electronic device operating both memory and display which stores and displays information

  - Current circuit

Internal connections of the meter and part of the measuring element through which flows the current of the circuit to which the meter is connected.

3.10	Voltage circuit

Internal connection of the meter part of the measuring element and power supply for the meter supplied with the voltage of the circuit to which the meter is connected.

  - Auxiliary circuit

Elements (lamps, contacts, etc) and connections of an auxiliary device within the meter are intended to be connected to an external device, for example clock, relay, and impulse counter.

  - Constant

Value expressing the relation between the energy registered by the meter and the corresponding value of the test output. If this value is a number of pulses, the constant should be either pulses per kilowatt-hour (imp.kWh) or watt hours per pulse (Wh/imp).

  - Indoor meter

Meter which can only be used with additional protection against environmental influences (mounted in a house, in a cabinet)	.

  - Outdoor meter

Meter which can be used without additional protection in an exposed environment

  - Base

Back of the meter by which it is generally fixed and to which are attached the measuring element, the terminals or the terminal block, and the cover.

  - Cover

Enclosure on the front of the meter, made either wholly of transparent material or opaque material provided with window(s) through which the operation indicator (if fitted) and the display can be read.

  - Case

Comprises the base and the cover

  - Protective earth terminals

Terminal connected to accessible conductive parts of the meter for safety purposes.

  - Terminal block

Support made of insulating material on which all or some of the terminals of the meter are grouped together.

  - Terminal cover

Cover which covers the meter terminals and generally, the ends of the external wires or cables connected to the terminals.

  - Clearance

Shortest distance measured in air between two conductive parts.

  - Creepage distance

Shortest distance measured over the surface of insulation between two conductive parts.

  - Basic insulation

Insulation applied to live parts to provide basic protection against electric shock.

  - Basic current (Ib)

Value of current in accordance with which the relevant performance of the meter is fixed

  - Maximum current (Imax)

Highest value of current at which the meter purports to meet the accuracy requirements of this standard

  - Reference voltage (Un)

Value of the voltage in accordance with which the relevant performance of the meter is fixed

  - Reference frequency

Value of the frequency in accordance with the relevant performance of the meter is fixed.

  - Percentage error

Percentage error is given by the following formula:

Percentage error = Energy registered by the meter – True Energy x 100

True Energy

Since the true value cannot be determined, it is approximated by a value with a stated uncertainty that can be traced to standards agreed upon between manufacturer and user or to national standards.

  - Reference conditions

Appropriate set of influence quantities and performance characteristics, with reference values, their tolerances and reference ranges, with respect to which the intrinsic error is specified

  - Electromagnetic disturbance

Conducted or radiated electromagnetic interference which may affect functionally or meteorologically the operation of the meter.

  - Rated operating conditions

Set of specified measuring ranges for performance characteristics and specified operating ranges for influence quantities, within which the variations of operating errors of a meter are specified and determined.

  - Specified measuring range

Set of values of a measured quantity for which the error of a meter is intended to lie within specified limits.

  - Specified operating range

Range of values of a single influence quantity which forms a part of the rated operating conditions

  - Limit range of operation

Extreme conditions which an operating meter can withstand without damage and without degradation of its metrological characteristics when it is subsequently operated under its rated operating conditions

3.35	Extended operating range

Extreme conditions which an operating meter can withstand without damage and without degradation of its metrological characteristics when it is subsequently operated under its rated operating conditions

  - Storage and transport conditions

Extreme conditions which a non-operating meter can withstand without damage and without degradation of its meteoric.

  - Normal working position

Position of the meter defined by the manufacturer for normal service

  - Thermal stability

Thermal stability is considered to be reached when the change in error as a consequence of thermal effects during 20 min. is less than 0.1 times the maximum permissible error for the measurement under consideration.

4.0	Performance standards

4.1	i.	Reference Temperature				23oC

ii.	Reference Frequency 				50 Hz

iii.	Reference voltages				3x230/400V

  - Climatic condition

-	Peak ambient temperature			50 oC

-	Mean Maximum temperature during 24 hours	45 oC

-	Minimum ambient air temperature		0 oC

-	Maximum relative humidity			95%

-	Minimum relative humidity			5%

-	Altitude					Sea Level

-	Location					Sea coast (interior is semi-desert)

-	Pollution					Severe marine pollution on account of 								windblown, sand and dust with salt content 							and salt laden spray and mist.

5.0	Mechanical requirements

5.1	General mechanical requirements

Meters shall be designed and constructed for Outdoor use in such a way as to avoid introducing any danger in normal use and under normal conditions, so as to ensure especially:-

- Personal safety against electric shock.

- Personal safety against effects of excessive temperature.

- Protection against spread of fire.

- Protection against penetration of solid objects.

- Protection against Dust and Water.

All parts which are subject to corrosion under normal working conditions shall be protected effectively. Any protective coating shall not be liable to damage by ordinary handling nor damage due to exposure to air, under normal working conditions. Meters shall withstand solar radiation test.

  - The electrical connections in the meter shall be resistant to tampering. These shall be made so as to prevent their opening from outside the meter base/cover accidentally or deliberately without breaking the seals.

  - Case

    - The meter shall have a reasonably dust proof and moisture proof case which can be sealed in such a way that the internal parts of the meter are accessible only after breaking the seals. The meter shall comply with the dust proof and water proof requirements of IEC-60529 amended to date.

5.3.2	Meter cover

The cover of meter shall either be made of clear or opaque shatter proof ultra violet stabilized polycarbonate material. In case of Clear polycarbonate material the electronics of the meter shall be protected with a shield inside the Meter Cover made of a suitable opaque material to protect the electronics from extreme environmental / especially solar radiation conditions.

    - Meter base

The base of the meter shall be made of strong insulating material.

5.4	Terminals – terminal block

    - The terminals shall be grouped in a terminal block having adequate insulating properties and mechanical strength. The material (Bakelite or similar material) of which the terminal block is made shall be capable of passing the tests given in ISO Standards 75 for a temperature of 135oC and glow wire test of 960oC.

    - Arrangements may be provided to prevent the exit of terminal block by force from outside without opening the meter cover.

    - The terminal shall be pressure plate type to permit the connection of both solid and stranded aluminum / copper conductor of cross sectional area 25 mm² to a depth of at least 20mm without being directly bitten by the screws used for fixing the conductors. The terminals in which screws bite directly into the conductor shall not be acceptable.

    - The moving parts of the terminals including screws shall be made of brass having minimum electrical conductivity of 65% of copper. The fixed part of terminal i.e. pressure plate shall be made of copper having a thickness of 2.4 mm and minimum electrical conductivity of 99.99% of stranded copper.

    - The terminals shall be Tin or Nickel plated. In case of Tin plating the thickness shall be 20 microns on all parts except threaded portions on which it shall be min 10 microns. In case of Nickel plating the coating thickness shall be 10 microns on all parts except the threaded portion on which it shall be min 7 microns.

5.5	Earthing connection arrangement

As the base is of insulating material, the common ground of the main PCB shall be internally connected to the neutral point of the terminal block.

  - Protection against heat, fire, penetration of dust & water, solar radiation.

The complete meter i.e. case terminal block shall meet the requirements of clauses 5.7 & 5.8 of IEC 62052-11. For protection against penetration of dust & water the meter shall be IP 54 complaint.

6.0	Electrical requirements

6.1	Standard ratings

Basic /max. Current		10/100 Amp

Reference Voltage		3x230/400 V

Reference Frequency		50 Hz

Accuracy Class			1.0

Meter Type	3-Phase, 3-Element, 4-Wire, Whole Current Meter suitable for recording the energy in a 4 wire system, neutral solidly grounded.

6.2	Other electrical requirements

Power Losses of voltage		2.0 W &

circuit at reference voltage	10 VA

Power Losses of Current

circuit at basic current		4 VA

Starting current			0.4% of Ib at unity power factor

Running with no load		From 0.8 to 1.15 of reference voltage but

with no current. Meter shall not produce

more than one pulse.

Temperature rise		25oC with ambient temp.

of external surface		of 45oC.

Temperature rise		30oC with ambient temp.

of terminal			of 45oC.

6.2.1	Dielectric strength

Power frequency 		4 KV for one minute

Withstand

Impulse voltage			8 KV: 1.2/50 micro

Withstand			sec & minimum 9 joules.

Short time over current		30 times Imax with a relative tolerance of

0% to -10% for ½ cycle at rated frequency.

Insulation resistance		More than 5 Mega Ohms

Creepage distance 		20 mm min.

  - Voltage range

Specified operating		From 0.9 to 1.1 of

Range				reference voltage.

Extended operating range	From 0.50 to 1.15.

Limit range of operation		From 0.002 to 1.9

of ref. voltage.

6.4	Accuracy requirement

6.4.1	Limits of error due to variation of the current

When the meter is under reference conditions given in clause 8.5 of IEC 62053-21, the percentage errors shall not exceed the limits given in Table-I & II.

Table - I

Percentage Error Limits With Balanced Loads

| Value of Current | Power Factor | Percentage error Limits for meters |
| --- | --- | --- |
| 0.05 Ib ≤ I < 0.1 Ib | 1 | ± 1.5 |
| 0.1 Ib ≤ I ≤ Imax | 1 | ± 1.0 |
| 0.1 Ib ≤ I < 0.2 Ib | 0.5 lagging 0.8 leading | ±1.5 ± 1.5 |
| 0.2 Ib ≤ I ≤ Imax | 0.5 lagging 0.8 leading | ± 1.0 ± 1.0 |
| 0.2 Ib ≤ I ≤ Ib | 0.25 lagging 0.5 leading | ± 3.5 ± 2.5 |

Table – II

Percentage error limits

(Meter carrying a single phase load but with balanced poly-phase voltages applied to the voltage circuits)

| Value of Current | Power Factor of the relevant element | Percentage error Limits for meters |
| --- | --- | --- |
| 0.1 Ib ≤ I < Imax | 1 | ± 2.0 |
| 0.2 Ib ≤ I ≤ Imax | 05 lagging | ± 2.0 |

The difference between the percentage error when the meter is carrying a single phase load and a 	balanced poly-phase load at basic current and unity power factor, shall not exceed 1.5%.

6.5	Influence of other quantities

6.5.1	Limits of error due to influence quantities:

The additional percentage error due to the change of influence quantities with respect to reference 	conditions, as given in clause 8.5 of IEC 62053-21 shall not exceed the limits given in Table-II.

Table – III

Influence Quantities

| Influence quantity |  | Value of current (balanced unless) otherwise | Power Factor | Limits of Variation in % age error for meters |
| --- | --- | --- | --- | --- |
| Voltage variation ±10% | 1) | 0.05 Ib ≤ I ≤ Imax 0.1 Ib ≤ I ≤ Imax | 1 0.5 lagging | 0.7 1.0 |
| Frequency variation ±2% | - | 0.05 Ib ≤ I ≤ Imax 0.1 Ib ≤ I ≤ Imax | 1 0.5 lagging | 0.5 0.7 |
| Reversed phase sequence | - | 0.1 Ib | 1 | 1.5 |
| Voltage unbalance | 3) | Ib | 1 | 2.0 |
| Harmonic components in the current and voltage circuits | 4) | 0.5 Imax | 1 | 0.8 |
| Odd harmonics in the AC current circuit | 4) | 0.5 Ib 2) | 1 | 3.0 |
| Sub-harmonics in the AC current circuit | 4) | 0.5 Ib 2) | 1 | 3.0 |
| Continuous magnetic induction of external origin | 4) | Ib | 1 | 2.0 |
| Magnetic induction of external origin 0.5 mT | 5) | Ib | 1 | 2.0 |
| Electromagnetic RF fields | - | Ib | 1 | 2.0 |
| Operation of accessories | 6) | 0.05 Ib | 1 | 0.5 |
| Conducted disturbances, induced by radio-frequency fields | - | Ib | 1 | 2.0 |
| Fast transient burst | - | Ib | 1 | 2.0 |

- For the voltage ranges from -20% to -10% and + 10 % to + 15% the limits of variation in percentage errors are three times the values given in Table-III.

Below 0.8 Un the error of the meter may vary between + 10% and -100%.

- The distortion factor of the voltage shall be less than 1%.

- Polyphase meters shall measure and register within the limits of variation in percentage error shown in Table-III if one or two phases of the 3-phase network are interrupted.

- The test conditions are specified in 8.2.1 to 8.2.4 of IEC 62053-21.

- A magnetic induction of external origin of 0.5 mT produced by a current of the same frequency as that of the voltage applied to the meter and under the most unfavorable conditions or phase and direction shall not cause a variation in the percentage error of the meter exceeding the values shown in the Table-III.

The magnetic induction shall be obtained by placing the meter in the centre of a circular coil, 1 m in mean diameter of square section and of small redial thickness relative to the diameter and having 400 At.

- Such an accessory, when enclosed in the meter case, is energized intermittently, for example the electromagnet of a multi-rate register.

It is preferable that the connection to the auxiliary device(s) is marked to indicate the correct method of connection. If these connections are made by means of plugs and sockets, they should be irreversible.

However, in the absence of those markings or irreversible connections, the variations of errors shall not exceed those indicated in this table if the meter is tested with the connections giving the most unfavorable condition.

    - Limits of error due to ambient temperature variation

The mean temperature coefficient shall not exceed the limits given in Table-IV.

Table - IV

Temperature Coefficient

| Value of Current | Power Factor | Mean Temp. Coefficient %K for meters |
| --- | --- | --- |
| From 0.1 Ib to Imax | 1 | 0.05 |
| From 0.2 Ib to Imax | 05 lagging | 0.07 |

6.5.3	Limits of error due to variation of the currents

When the meter is under reference conditions given in clause 8.5 of IEC 62053-23. The 	percentage 	errors shall not exceed the limits given in Table V & VI.

Table – V

Percentage error limits with balanced loads

| Value of Current | Sin  (Inductive) | Percentage error limits |
| --- | --- | --- |
| 0.05 Ib < I <0.1 Ib | 1 | +2.5 |
| 0.1 Ib < I < Imax | 1 | +2.0 |
| 0.1 Ib < I <0.2 Ib | 0.5 | +2.5 |
| 0.2 Ib < I < Imax | 0.5 | +2.0 |
| 0.2 Ib < I < Imax | 0.25 | +2.5 |

Table – VI

Percentage error limits (meter carrying a single phase load but with balanced poly-phase voltages 	applied to the voltage circuits)

| Value of Current | Sin  (Inductive or capacitive) | Percentage error limits |
| --- | --- | --- |
| 0.1 Ib < I < I max | 1 | + 3.0 |
| 0.2 Ib < I < I max | 0.5 | + 3.0 |

The difference between the percentage error when the meter is carrying a single phase load 	and a balanced poly phase load at basic current Ib and sin  = 1 shall not exceed 2.5%.

The energy for inductive load be recorded and should register the absolute some of quadrant           	1 & 3.

6.5.4	Limits of error due to influence quantities

The additional percentage error due to the change of influence quantities with respect to reference 	conditions, as given in 8.5 of IEC 62053-23 shall not exceed the limits given in Table-VII.

### Table-VII

#### Influence Quantities

| Influence quantity | Value of Current (balanced unless otherwise stated) | Sin  (Inductive) | Mean temperature coefficient % K for Meters of class 2 |
| --- | --- | --- | --- |
| Ambient temperature Variation 7) | 0.1 Ib < I < I max 0.2 Ib < I < I max | 1 0.5 | 0.10 0.15 |
|  |  |  | Limits of variation in Percentage error for Meters of class 2 |
| Voltage variation +10% 2) | 0.05 Ib < I < I max 0.1 Ib < I < I max | 1 0.5 | 1.0 1.5 |
| Frequency variation +2% 2) | 0.05 Ib < I < I max 0.1 Ib < I < I max | 1 0.5 | 2.5 2.5 |
| DC component in the current circuit 3) | Imax 2 | 1 | 6.0 |
| Continuous magnetic induction of external origin 4) | Ib | 1 | 3.0 |
| Magnetic induction of external origin 0.5 mT 5) | Ib | 1 | 3.0 |
| Electromagnetic RF Fields | Ib | 1 | 3.0 |
| Operation of accessories 6) | 0.05 Ib | 1 | 1.0 |
| Conducted disturbances, induced by radio-frequency fields | Ib | 1 | 3.0 |
| Fast Transient burst | Ib | 1 | 4.0 |

- For the voltage ranges from –20% to 10% and +10% to +15%, the limits of variation in percentage errors are three times the values given in this Table-VII.

Below 0.8 Un the error of the meter may vary between +10% and -100%.

2)	The recommended point for voltage variation and frequency variation is Ib for direct connected meters.

3)	The purpose of this test is to check for current sensor saturation only.

4)	The test conditions are specified in 8.2.2 of IEC 62053-23.

5)	A magnetic induction of external origin of 0.5 mT produced by a current of the same frequency as that of the voltage applied to the meter and under the most unfavorable conditions of phase and direction shall not cause a variation in the percentage error of the meter exceeding the values shown in this Table.

The magnetic induction shall be obtained by placing the meter in the centre of a circular coil, 1 m in mean diameter, of square section and of small radial thickness relative to the diameter, and having 400 At.

- Such an accessory, when enclosed in the meter case, is energized intermittently, for example the electromagnet of a multi rate register.

It is preferable that the connection to the auxiliary device(s) is marked to 	indicate the correct method of connection. If these connections are made by means of plugs and sockets, they should not be interchangeable.

The mean temperature coefficient shall be determined for the whole operating range. The 	operating	temperature range shall be divided into 20 K wide ranges. The mean temperature 	coefficient shall 	then be determined for these ranges, by taking measurements 10 K above and 10 	K below the 	middle of the range. During the test, the temperature shall be in no case outside the specified 	operating temperature range.

  - Meter Constant

The relation between the test output and the indication in the display shall comply with the marking on the name plate.

Output devices generally do not produce homogeneous pulse sequences. Therefore, the manufacturer shall state the necessary number of pulses to ensure a measuring accuracy of at least 1/10 of the class of the meter at the different test points.

7.0 	Meter characteristics

The meter shall generally comprise of the following characteristics as a minimum. A list of characteristics is appended below:

7.1 	Basic data recording and storage

7.1.1 	Static KWH & KVARH Multi-Rate Meter

- Energy (KWh).

- Reactive energy (kvarh).

- Max. Demand (KW), shall be block type.

- Demand Interval shall be 30 minutes, however it shall be programmable for other values also.

- Cumulative Max. Demand (KW).

- There should be a separate LED for testing and calibration of Reactive energy.

- At-least twelve months Billing Data kWh, kvarh, KW and number of resets shall be available at all times.

- Min. Four Multi rate periods Energies (KWh).

- Min. Four Multi rate periods Max. Demand (KW).

- Min. Four Multi rate periods Cumulative Max. Demand (KW).

- Min. Four Multi rate periods Reactive Energies (kvarh).

- Min Two Seasons per year should be programmable.

- Min 100 days per year holidays should be programmable.

7.1.2	Load profiling/recording:

- Min. Two load profiles’ recording having sufficient capacity to record at-least 65 days of Data of 30 minutes interval. Minimum quantities to be recorded are (A+, A-, R+, R-, S+,S-, phase currents(L1,L2,L3), phase voltages(L1,L2,L3) and phase PFs(L1,L2,L3)

- The load profiles must be configurable and the quantities could be added or removed as per requirement through meter software.

- After downloading Load Profile Data in computer through reporting software, it should be available in tubular form.

- There should be date and time stamp for every entry of Load Profile data.

- All Load Profile Data shall be stored in a Non-Volatile Memory.

7.1.3 	Back-up battery

- The Back-up Battery shall be of Lithium-Ion type.

- Low Battery indication shall be displayed when min. 25% battery life is left.

- Storage life of Battery shall be more than 15 years.

- Without any Power the Back-Up battery shall maintain the time, calendar, Multi-Rate program & function of LCD display during power outage for a continuous period of at-least 24 months.

- The battery shall be connected using standard connectors, it shall not be welded, brazed or 	soldered.

7.2 	Security Features, Event Recording and Diagnostics:

7.2.1 	Features

- Every Meter shall have a unique serial No. in its memory which can be displayed/reported.

- The No. of times programmed and the identification of the last programmer along with Date & Time stamp shall be reported/displayed.

- A programmable meter ID code shall be provided.

- At-least two levels of access/security codes shall be provided one for meter reading (only) by the authorized personnel and a second one for programming and reading.

- Meter shall keep on recording/operating as long as voltage exists on any two terminal of the meter with or without neutral.

- The meter shall be protected against any external interference such as influence of Strong Electromagnet, CD drive and Mobile phones and shall comply to all relevant IEC/ANSI standards for functional performance and loss of data.

- A strong magnet having strength of 0.7 Tesla, when measured in an air gap of 3mm, rectangular in shape with minimum dimension of 65 x 35 x 35mm shall not affect the accuracy of meter by more than 4% at Basic Current and Unity Power Factor when applied on the meter from any direction. After the test meter shall perform within prescribed limit of Accuracy.

7.2.2 	Security features

- Total No. of power outages.

- Phase failure/Disconnection of wires.

- Reverse energy flow of active and reactive energy.

- Reverse polarity.

- Programming event.

- At-least 100 total events shall be recorded in the meter at any one time before Roll Over they may comprise of the above or any additional features.

7.2.3 	Diagnostics

The meter shall display cautions and diagnostics for the following conditions:

- Un-programmed Meter.

- Self check diagnostics for RAM/ROM, Processor, non-volatile memory failure and

other essential hardware circuitry.

7.3	Display

- The Display shall be LCD type with at-least (06) digits for Energy consumption.

- Display scrolling time shall be programmable.

- Min. three programmable Display modes shall be available.

- First Display mode shall be the Normal or Automatic display mode. Second display mode shall be for Security / Diagnostics etc. The third Display mode shall be for Test Purposes. Activation of Display Mode shall either be with a secure Push Button or an equally secure alternate method.

- Phase Indicators shall be permanently displayed in all Display modes.

- All Segment Check.

- Display Mode Indicator.

- Display Quantity Labels.

- Pulse Output for field testing of Meter shall be available optically.

- The battery shall be able to display all the quantities selected for normal mode display during power supply failure through use of push button.

- The meter shall have forward and reverse scroll capability.

- I/O interface (optional),

- Data retrieval in case of power OFF (optional).

7.4 	Meter Programming, Software and Security

The following features shall be programmable in the meter as a minimum along-with other features that may be provided:

- Demand Time interval (1, 10, 15, 30, 60 minutes).

- Demand resets shall be configured for automatic resets on a preset date to override the manual reset.

- The meter shall have non-volatile EEPROM memory.

- Once programmed the meter shall be re-programmable as a new meter with all reading/registers reset to zero (0).

- Meter programming shall be Windows based.

- An Optical Communication Port shall be provided on the meter cover and shall either be IEC 62056-21 or ANSI C12.18 Type II compliant.

7.5       Communication Modem

Communication Modems must be pluggable/built in type and should be completely protected by the terminal cover or inside the main cover of the meter and should be auto-supplied by the meter.

The modem shall initiate a message/notification in the event of any tamper being logged by the meter and shall be able to send the relevant data to AMM system immediately such as:

- Inactive phase current.

- Voltage phase deviation.

- Inactive phase.

- Energy polarity current.

Modem must be easily configurable through modem software.

The modem must be accessible remotely standard commands and must be password protected

7.6	Remote reconnect/disconnect

Scenario-1: Disconnection due to Non-Payments

Meter must accept disconnection/reconnection command by backend system remotely as and when required. In case of disconnection initiated by backend system, meter should not reconnect unless received reconnection command by backend system.

Scenario-2: Disconnection against Load Limiting/Exceeding sectioned Load

Two different load thresholds against different time slots, must be programmed to activate disconnection/reconnection automatically by the meter and time between disconnection and reconnection must also be programmable.

Meter should have the capability to change load thresholds and associated time slots remotely

8.0	Peripheral devices

8.1	Optical probe

The optical probe shall be used to transfer data to and from the meter. The probe shall have an optical head on one end to interface with the meter and a USB connector on the other end to connect directly with the PC. The communication through optical probe shall conform to protocol IEC‐62056‐21 Data Exchange for Meter Reading, Rate and Load Control.

8.2	Support system requirements for meter software

The meter software shall be Windows NT/2000/XP based and would be supplied free of cost. It would have following (but not limited to) features.

- Monitoring / reading of all registers.

- Diagnostic / troubleshooting / setting / configuration.

- Configuring the meter shall be controlled locally via access code/password.

The software shall be a user friendly, menu driven. The software shall have provisions to create 	user and configure different access levels for the user.

Meter should be capable of upgrading software /firmware through remote connection.

The meter should communicate “Total power break down” event as soon as it occurs. Back up battery or super capacitor may be used for this communication.(optional)

The meter should be capable of recording terminal cover opening event & main cover opening event even during total breakdown condition. The same may be communicated immediately or recorded and communicated when power is ON. (optional)

9.0	Type test

9.1	Type test shall be carried out on AMR solid state energy meters at an independent accredited laboratory like KEMA of Holland, CESI Italy, CRIEPT Japan. Criteria of selection of samples and    acceptance / rejection shall be as per relevant IEC.

Following type tests shall be carried out on KWH & KW meters as per respective IECs.

    - Tests of mechanical requirements:

- Spring hammer test.

- Shock test.

- Vibration test.

- Test of resistance to heat and fire.

- Test of protection against penetration of dust and water.

    - Test of climate influence:

- Dry heat test.

- Cold test.

- Damp heat cycle test.

- Solar Radiation test.

    - Tests of electrical requirements:

- Test of power consumption of voltage circuit.

- Test of power consumption of current circuit.

- Test of effect of voltage dips and short interruptions.

- Test of influence of short time over current.

- Test of influence of self heating.

- Test of influence of heating.

- Impulse voltage test.

- A.C. voltage test.

    - Tests for electromagnetic compatibility (EMC):

- Test of immunity to electrostatic discharges.

- Test of immunity to electromagnetic HF fields.

- Fast transient burst test.

- Radio interference measurement.

    - Tests of Accuracy requirements (for KWH meter parts as per

IEC 62053-21 where applicable:

- Test of Accuracy.

- Test of influence quantities.

- Test of no load condition.

- Test of starting condition.

10.0	Name and rating plate

  - A suitable name/rating plate shall be provided inside at the front of the meter, indicating the 	following information:

- Name of the manufacturer and country of origin.

- Type of meter.

- Number of phases and number of wires.

- Nominal and maximum current, nominal voltage and frequency.

- Accuracy class.

- Meter constant.

- KESC P.O. No.

- KESC Meter No. and year of manufacturer.

- KESC property, not for sale.

- Display sequence should be printed on nameplate.

- SAP code.

11.0	Packing

Each meter shall be individually packed in thermo pore packing or thermo pore lined packing, covered with adhesive tape at joints or plastic strips etc.

The packing shall be strong enough to withstand rigors of ocean, rail, road etc.

12.0	Sample

At least three number samples of meter shall be submitted with the bid.

13.0	Pre-shipment inspection

The successful bidder shall offer the meters for testing/inspection, Procedure for pre-shipment 	inspection is given below:

13.1	Routine tests

Following routine tests shall be carried out on KWH, KW meters as per respective IECs by the manufacturer:

- Accuracy Test.

- Running with no load test.

- Starting current test.

- Insulation resistance test.

13.2	Sample tests

13.2.1	The sample tests (Electrical & Mechanical) are intended to verify compliance of the characteristics 	of the meter with the relevant requirements of this specification. The tests shall be carried out at 	manufacturer works in 	the presence of KESC engineers. All expenditure regarding air ticket, 	boarding, lodging etc. shall be 	borne by the bidder. Criteria of 	selection of samples and 	acceptance / rejection shall be as mentioned below.

13.3	Tests

13.3.1	Sample tests (electrical)

13.3.1.1The meters offered for acceptance shall be grouped into lots containing upto 1000 meters. A 	sample comprising of five (05) meters shall be selected at random from each lot and subjected to 	tests as 	below:

Starting current test

Creep test

Accuracy test

A.C. voltage test

13.3.1.2 The meters offered for acceptance shall be grouped into lots containing upto 1000 meters. A 	sample comprising of two (02) meters shall be selected at random from each lot and subjected to 	following tests:

Impulse test

Power loss test

Fast transient burst test

Influence of harmonics test

DC and even harmonics test

Dry Heat Test at 80oC

13.3.1.3The lot shall be accepted if all the meters qualify in the tests described in clause 13.3.1.1 & 13.3.1.2 	above. The lot shall be rejected if two or more meters fail in any of the tests. If any one meter fails 	in any of the above tests re-sampling shall be carried out after collecting same No. of meters 	and subjected to the tests described in clause 13.3.1.1 & 13.3.1.2 above. If any one meter fails in 	any of the above tests the whole lot shall be rejected.

13.3.2 	Sample tests (mechanical)

13.3.2.1The meter offered for acceptance shall be grouped into lots containing upto 1000 meters. Sample 	comprising of  two (02) meters shall be selected at random from each lot and subjected to tests as 	below:

Sr. No		Description 					Nos. of Meters

1. 		Test of protection against penetration of

dust and water.					One meter

2.		Dimensional Check.				One meter

13.3.2.2 The lot shall be accepted if meters qualify the above tests in clause 13.3.2.1. In case any meter fails in the relevant test, another sample of double the size shall be selected and test/tests repeated If any meter fails in the relevant in the second group, the entire lot shall be rejected.

13.4 	Verification test of functionality of software

13.4.1	Verification test of the functionality of software and display features on offered meters shall be 	promoted by loading/unloading of program and auditing the diagnostic reports. The number of 	meters shall be three if any meter fails to comply with the functionality requirements the entire 	offered lot shall be rejected.

13.5	The remaining type tests not performed on the above samples shall be carried out (as per 	recommended sequence of IEC 62052-11 annexure-F on three (03) Nos. meters out of the total 	offered meters. If two meters fail in any of the above tests, the lot shall be rejected. If one of the 	meters fails to qualify any of the above tests, re-sampling shall be carried out, in case of failure of 	any of the tests the lot shall be rejected.

14.0	Warranty.

The supplier shall provide two years warranty for the successful operation of the meter including its maintenance whenever required. Any change suggested by the user/evaluation committee in the reporting software shall be accommodated. The defective meters shall be replaced with new ones free of cost within warranty period.

15.0	Possibilities for acceptance / rejection of bid.

KESC retains the right to accept or reject offers which are not in accordance with one or more requirements of this technical specification. Similarly KESC may consider offers where exceptions are highlighted by the vender if it feels these exceptions may be considered acceptable in certain circumstances.

16.0	Training.

The successful bidder shall arrange comprehensive practical training regarding, trouble-shooting programming, billing, loading of software etc. at manufacturer works or in KESC on his own cost.

17.0	Bid Data, Test Certificates, Drawings, Literature, Reference List & Manufacturing Experience

All the bidders shall submit complete technical data, detailed drawings test certificates, literature in English language, supply reference list and manufacturing experience along with the bid.

The following should accompany the bid:

- i)	Constructional drawing indicating the dimensions of the meters.

- ii)	Detailed description of the meter.

- iii)	Constructional and test regulations as well as their Test certificates.

- iv)	Certificate of ISO 9001 or 9002 for the factory standards.

v)	Meter’s connection in 3-phase 4-wires.

vi)	Diagram for signal processing.

vii)	Schematic diagram for the Energy registers.

18.0	List of display items in TOU meter normal mode

18.1	Normal mode (same items shall be displayed during power outage)

All segment check

- Meter ID

- Date

- Time

- Present tariff A kWh

- Present tariff B kWh

- Present tariff A max. kW

- Present tariff B max. kW

- Previous tariff A max. kW

- Previous tariff B max. kW

- Error code

Alternate mode

All segment check

- Meter ID

- Date

- Time

- Present total kWh

- Present tariff A kWh

- Present tariff B kWh

- Present total kvarh

- Present tariff A kvarh

- Present tariff B kvarh

- Present tariff A max. kW

- Present tariff B max. kW

- Previous tariff A max. kW

- Previous tariff B max. kW

- Instantaneous kW

- Phase A voltage

- Phase B voltage

- Phase C voltage

- Phase A current

- Phase B current

- Phase C current

- Power factor

- Frequency

- Error code

Note:	Display items in normal & alternate mode are programmable. Normal mode shall be print on 	nameplate of meter. Number of rate will be applicable as defined by KESC.

19.0	Operation Instructions

The bidders must deliver with their offers a copy of the operation manual and the supplier must deliver 10 copies of the above manual during the first delivery

20.0	Manuals for Maintenance & Repair

The bidders must deliver with their offer manuals for maintenance and repair including instructions for check and regulation and the necessary software.

Additionally the supplier must deliver troubleshooting list with the method “step by step” and diagrams of the internal wiring within 15 days from the signature of the contract.

21.0	Possibilities for Acceptance / Rejection of Bid

KESC retains the right to accept or reject offers which are not in accordance with one or more requirements of this technical specification. Similarly KESC may consider offers where exceptions are highlighted by the vender if it feels these exceptions may be considered acceptable in certain circumstances.

22.0	Disclaimer

The subject specification(Annex II) are according to current AMM/communication systems and 	would be modified accordingly if any change will occur in AMM/communication systems.

Annex - I

Reference standards

When following standards referred to in this document have been superseded, the latest revisions shall apply:

1.	Metering standards

a.	IEC

62053-21 : 2003,	Static Meters for Active Energy (Classes 1 & 2).

61358 (1996-05)	Acceptance inspection for direct connected alternating current

static watt-hour meters for active energy (Classes 1 & 2).

62052-11 : 2003	Electricity Metering Equipment (AC) – General Requirements,

Tests and Test conditions

61162, 61107		Optical interface

b.	ANSI

C12.18			Protocol specification for ANSI type II Optical ports.

C12.19			Utility industry and device data tables

2.	Electrical testing standards

a.	IEC

60038:1983,		IEC standard voltages

50(301, 302, 303) : 1983, International Electro technical

Vocabulary (IEV) Chapter 301: General terms on measurements in

electricity. Chapter 302: Electrical measuring instruments.

Chapter 303:Electronic measuring instruments.

60060-1 : 1989		High voltage test techniques

60085 : 1984		Thermal evaluation and classification of electrical insulation.

61000-4-2 : 1995	Electromagnetic compatibility (EMC)-Part 4: Testing &

measurement techniques-section 2: Electrostatic discharge

immunity test.

61000-4-3 : 2002	Electromagnetic compatibility (EMC) – Part 4-3: Testing &

measurement techniques-section 2: Radiated radio frequency

electromagnetic field immunity test.

61000-4-4 : 1995,	Electromagnetic compatibility (EMC)-Part 4: Testing &

measurement techniques-section 4: Electrical fast transient/burst immunity test.

CISPR22: 1997,	Information technology equipment-Radio disturbance

characteristics-limits & methods of measurement

b.	ANSI

C37.90.1 – 1989,	IEEE standard surge withstand capability.

C62.41 – 1991,		IEEE recommended practice on surge voltages in Low-voltage AC

power circuits.

3.	Mechanical testing standards

a.	IEC

60529 : 1989,		Degrees of protection provided by enclosures (IP code).

60695-2-11 : 2000,	Fire hazard testing, Part 2-11: Glowing/hot wire based test

methods.

60817 : 1984,		Spring operated impact test apparatus and its calibration.

b.	ISO Standard

75-2 : 1993,		Plastics – Determination of temperature of deflection under load –

Part 2: Plastic & ebonite.

4.	Environmental standards

a.	IEC

60068-2-1 : 1990,	Environmental testing, Part 2: Tests. Tests A: Cold.

60068-2-2: 1974,	Basic environmental testing procedures, part 2: Tests. Tests B: Dry

Heat.

60068-2-5: 1975,	Basic environmental testing procedures, part 2: Tests. Test Sa:

Simulated solar radiation at ground level

60068-2-6 : 1995,	Environmental testing, part 2: Test. Test Fc: Vibration (sinusoidal).

60068-2-11 : 1981,	Basic environmental testing procedures, part 2: Tests. Test Ka: Salt

mist

60068-2-27 : 1987,	Basic environmental testing procedures, part 2 : Tests. Test Ea and

guidance: Shock

60068-2-30 : 1980,	Basic environmental testing procedures, part 2: Tests. Test Db and

guidance: Damp heat, cyclic (12 + 12-hour cycle).

60721-1 : Ed.2.0 b	Classification of environmental conditions. Part 1: Environmental

parameters and their severities.

60721-2-1 (1982-01)	Classification of environmental conditions. Part 2: Environmental

conditions appearing in nature. Temperature and humidity.

60721-2-4 (1987-12)	Classification of environmental conditions. Part 2: Environmental

conditions appearing in nature. Solar Radiation and temperature.

KESC AMM System (Annexure-II)

KESC AMM (Automated Metering Management) System consists of meter data acquisition and metering data management system that communicates with field devices over VPN based upon GPRS. One of the most important requirements is the compatibility of offered AMR meter with KESC AMM system and SAP ISU billing Engine.

GPRS Modem:

GPRS Modems must be pluggable type or built in and should be completely protected by the terminal cover or inside the main cover of the meter.

The modem shall  be auto-supplied by the meter itself.

The modem must have standard SIM interface.

The modem must support VPN (Virtual Private Network) means that APN could be set.

The modem must support SIMs with static IP

The modem shall initiate a message/notification in the event of any tamper being logged by the meter and shall be able to send the relevant data to the KESC AMM system immediately such as:

- Inactive phase current.

- Voltage phase deviation.

- Inactive phase.

- Energy polarity current.

Modem must be easily configurable through modem software and modem software must be in English language.

The modem must be accessible remotely over VPN by standard telnet commands or by meter software or modem software and must be password protected. Modem must be capable to report signal strength remotely over VPN by telnet commands or meter software or modem software.

Meter Software:

Meter software should be capable to communicate with meter remotely over VPN based upon GPRS as well. Meter software must have the capability to read LPs, meter time, log book and time synchronization over VPN based upon GPRS. Meter software must be capable of parameterization of meter (LP reconfiguration, reprogramming of Tariff, Display, DRO etc.) remotely over VPN based upon GPRS with security passwords.

KESC AMM System Manufacturer: Pre-Requisites:

- The offered AMR meter must be either DLMS/COSEM compliant or IEC 62056-21 (Former 1107) compliant. The following billing/load profile data is required to be fetched by AMM in addition to alarms/events and meter time read/synchronization.

Billing Registers:

ActiveEnergyPlus_CUM_T0,T1,T2

MaximumDemandActivePlus_T0, T1&T2

ReactiveEnergyPlus_CUM_T0, T1&T2

LP1:

Power Registers (A+, A-, R+, R-, S+, S-) with last average

LP2:

Phase currents, phase voltages, phase PFs

- Load profile values (records) must have associated status codes for automatic billing by SAP ISU billing engine. Status codes for load profile records are required against following events at minimum.

Measuring device error

Measuring device battery discharged

Periodic or manual reset of billing values

Summer/winter time or winter/summer time change

Longer measurement period, time synchronization

Shorter measurement period, time synchronization

Power restored during measurement period

Power failure during measurement period

Valid Value

Each status code will be Hex sum of all events associated to the corresponding record.

Sample Load Profile with Status Codes:

| Time | Status | A+ [kW] | A- [kW] | R+ [kvar] | R- [kvar] | S+ [kVA] | S- [kVA] |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1/6/2012 14:00:00 | 00000000 | 98 | 0 | 17.2 | 0 | 99.6 | 0 |
| 1/6/2012 14:30:00 | 00000000 | 213.2 | 0 | 44.8 | 0 | 218.8 | 0 |
| 1/6/2012 15:00:00 | 000000C0, Power down, Power up | 34.4 | 0 | 17.2 | 0 | 44 | 0 |
| 1/6/2012 15:30:00 | 00000080, Power down | 12 | 0 | 6.4 | 0 | 14.4 | 0 |
| 1/6/2012 17:30:00 | 00000040, Power up | 0 | 0 | 0 | 0 | 0 | 0 |
| 1/6/2012 18:00:00 | 00000000 | 155.6 | 0 | 35.2 | 0 | 160.4 | 0 |
| 1/6/2012 18:30:00 | 00000000 | 165.2 | 0 | 40.8 | 0 | 170.4 | 0 |

Integration of 3rd Party Meter with KESC AMM System:

The following functionality of meters would be implemented into AMM System.

-  Data reading (Indexes, LP) along with LP status codes
-   Events’ Log reading
-   Alarm functionality

-   Translation of LP status codes of meters into AMM codes
-   Meter time read and synchronization

-   Remote Disconnect/Reconnect

-   Reprogramming of threshold (KW) for sanctioned load

-  Reprogramming of threshold s (KW) against different time slots of a day for load limiting to     serve the purpose of cutting peak demand

Meter Manufacturer will have to provide the following items but not limited to:

-  Two samples of each meter type to be integrated

- Specifications of communication protocol of IEC 62056-21 or DLMS/COSEM which ever  meter supports

- Description of object implementation along with event enumeration

Schedule of technical data

Three phase direct online static energy meters

5kw & above

(accuracy class-1)

A.          General

1.	Bidder's name & Address

2.	Manufacturer's name &	Address

3.	Manufacturing Experience

# B.         Energy meters

- Model No. / Type

- Basic current

- Maximum current

4.	Minimum starting current at ref. Voltage & ref. Frequency

5.	Operating voltage

6.	Overload capacity

7.	Accuracy class

i.	kWh Meter

ii.	MDI

iii.	kvarh

8.	No. of elements

9.	Detail of:

i.	kWh part

ii.	MDI part

10.	Losses in

i)	Potential Ckt

ii)	Current Ckt

11.	Encapsulation Details

i)	Current Sensor

ii)	Class of Insulation

12.	Max. current that meter

can withstand during short

circuit for 0.5 second.

13.	Dielectric strength

i)	Impulse Voltage

ii)	C test Voltage

14.	Insulation resistance of meter.

15.	Material of:

a.	Base

b.	Cover

c.	Security Box

d.	Terminal Block

e.	Terminals

f.	Printed Ckt Board

(All the above shall be indicated on drawings to

be supplied with the bid.)

16.	Temperature rise of meter

17.	Type of terminals

18.	Centre to centre clearance

between different phases

a.	Creepage Distance

b.	Clearance

19.	Whether the meter is compliant to the

reference standards for testing mentioned

in Annex -I of the specs.

20.	Whether the meter have the

following characteristics:

a.	Basic data recording and storage;

(as per clause 7.1 of the spec.),

give details.

b.	Security Features, Events recording

and Diagnostics; ( as per clause 7.2

of the spec.), give details.

c.	Display

(as per clause 7.3 of the spec.),

give details.

d.	Back-up Battery;  (as per clause 7.1.3 of the spec.)

give details

e.	Meter Programming, Software and Security;

(as per clause 7.4 of the spec.)

give details

21.	Operating ambient temp. range.

a.	Specified Operating Range

b.	Limit Range of Operation (Extreme Condition)

c.	Limit range for storage and Transport

22.	Size & No. of digit of LCD Display.							.

23.	What is the sampling rate.

24.	IP class of meter

25.	No. of digits for following features;

i)	kWh

ii)	kvarh

iii)	Demand kW

iv)         Cumulative kW

v)	No. of Reset digits

26.	What values / readings are

controlled through resetting device?

27.	Detail of resetting device with

sealing arrangement (give drawing).

28.	Min. No. of rate/rates for

which the rate register can be

programmed for:

-kWh

-kvarh

-kW

29.	Effect of external magnetic

field as per IEC 62053-21.

30.	Effect of Radio frequency signals.

31.	Effect of Influence of DC and Even Harmonics

as per IEC 62053-21.

32.	Effect of other Influence Qty. as per IEC

33.	Type of Meter Memory

34.	Storage capacity of memory

35.	Time to retain the memory

36.	In case of error in register

Which types of checks are

Provided which automatically

Identifies the error

37.	Meter Clock:

a)	Source of operation of

Built in clock

b)	Effect of variation of

Frequency of source

c)	Source of operation of

Clock in case of power outage

d)	If battery is used what

Is the life of  battery

e)	Period / life for which the

battery can supply power

continuously to check and

register prior to its

Discharge below 25%.

g)	No. of programmable dates

to account for holidays and

week ends

38.	The Meter Programming/Reading Software

is Windows

39.	Name / Rating Plate;

Detail of information given on

Name Plate

40.	Attachments

Whether the following material has been attached;

a.	Accuracy Curves

b.	Drawings of meter showing

dimensions, mounting

details etc

41.	Bidders / manufacturers have to supply

all relevant drawings & technical

literature duly marked

42.	Details of the deviations of the offered

equipment from specification (use

separate sheet if required

Signature & Seal of

Bidder / Manufacturer